Kilbeggan (KBNB)

Wednesday 1 April 2026

10:31

Low Voltage: NO Alarms visible to SMC

High Temperature alarm: NO Alarms visible to SMC

Low Voltage and High-Temperature alarms are NOT visible to SMC

High Battery Temperature alarm on Power One not visible to SMC

Please clean/replace filter on Nokia KBN-MSAN.

## Do Three Month Routine for Battery 1 in Kilbeggan

Overall voltage: 54.24

Cell 1 - 13.49

Cell2 -13.57

Cell 3 - 13.57

Cell 4 - 13.59

## Do Three Month Routine for Battery Feeding NGN Equipment in Kilbeggan

Overall: 54.11

13.46

13.51

13.57

13.54

## Do DC Power Routine in Kilbeggan

Rectifiers: 6

DC Load: 18.5 A

Boost Voltage: 54.0

Float Voltage: 54.64

Low Voltage: 47V

High Temperature: 30 °C

Low Voltage and High Temperature alarms were tested, but only Low Voltage was detected.

## Do DC Power Routine Feeding NGN Equipment in Kilbeggan

Rectifiers: 5

DC Load: 21 A

Boost Voltage: 54.5

Float Voltage: 54.2

Low Voltage: 47V

High Temperature: 30 ° C

Low Voltage and High-Temperature alarms are not visible to SMC.