Kinnity - (KNTA)

Wednesday 11 March 2026

11:47

Please clean/replace filter on Nokia KNT-MSAN

Battery temperature: 13 °C

Overall Voltage: 53.99

Cell 1: 13.57

Cell 2:13.50

Cell 3: 13.54

Cell 4: 13.48

| Rectifiers | 6 |
| --- | --- |
| DC Power Load | 16.2 |
| Boost Voltage | 54 |
| Float Voltage | 53.79 |

### Alarm Limits

| Low Voltage | 47V |
| --- | --- |
| High Voltage | 58 |
| High Load | 100% |
| High Temperature | 30 °C |

Low Voltage, High Voltage, High Load and High Temperature alarms were tested, but only Low Voltage alarm was visible to SMC