Daingean (DGNB) - ;dangen;

Monday 23 February 2026

11:13

Batteries 2 and 3 has been removed

Battery has been removed from the exchange

Please clean/replace filter on Nokia DGN-MSAN.

Inspect FAN on FTTH node DGN1_F01A of terminal & fibre/exhaust clear - Visual chk of terminal & fibre

No alarm visible to SMC

## Do Three Month Routine for Battery 1 in Daingean

Temp: 20 C

Overall Voltage: 54.11

| Cell | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Volts | 2.24 | 2.2422 | 2.423 | 2.423 | 2.236 | 2.237 | 2.257 | 2.237 | 2.237 | 2.237 | 2.227 | 2.22 | 2.26 | 2.24 | 2.25 | 2.32 | 2.36 | 2.3 | 2.327 | 2.347 | 2.357 | 2.357 | 2.42 | 2.426 |

## Do DC Power Routine for Rectifier

| Rectifiers | 5 |
| --- | --- |
| DC Load | 23 |
| Boost Voltage | 53.5 |
| Float Voltage | 54.21 |
| Temperature | 20 |

Alarm Limits

| Low Voltage | 46.3 |
| --- | --- |
| High Voltage | 59.5 |
| High Load | 80% |
| High Temperature | 30 °C |

Low Voltage, High Voltage, High Load and High Temperature alarms were triggered,

only one was detected as a Power Alarm.

## Do DC Power Routine for Rectifier Feeding NGN Equipment in Daingean

| Rectifiers | 4 |
| --- | --- |
| DC Load | 16 |
| Boost Voltage | 54.5 |
| Float Voltage | 54.55 |
| Temperature | 19 |

Alarm Limits

| Low Voltage | 47 |
| --- | --- |
| High Voltage | 58 |
| High Load | 80% |
| High Temperature | 30 |

Low Voltage, High Voltage, High Load and High Temperature alarms were triggered,

only one was detected as a Power Alarm.

## NGN batteries

Temp: 19 C

Battery 1 - Overall voltage: 54.576

| Cell 1 | Cell 2 | Cell 3 | Cell 4 |
| --- | --- | --- | --- |
| 13.64 | 13.64 | 13.62 | 13.62 |

Battery 2 - Overall voltage: 54.53

| Cell 1 | Cell 2 | Cell 3 | Cell 4 |
| --- | --- | --- | --- |
| 13.70 | 13.57 | 13.56 | 13.67 |