Mountmellick (MMKA)

Wednesday 14 January 2026

11:40

14 routines

Please clean/replace filter on MMK-MSAN

Battery 2 has been removed

## Do Three Month Routine for Battery 1 in Mountmellick

Overall Voltage: 53.57V

Temperature: 23 °C

| Cell | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | 2.17 | 2.23 | 2.22 | 2.24 | 2.26 | 2.22 | 2.14 | 2.19 | 2.22 | 2.22 | 2.21 | 2.18 | 2.2 | 2.21 | 2.21 | 2.1 | 2.23 | 2.26 | 2.23 | 2.2 | 2.29 | 2.26 | 2.28 | 2.28 |

## Do Three Month Routine for Battery 2 in Mountmellick

Battery has been removed.

## Do DC Power Routine in Mountmellick

| Rectifiers | 7 |
| --- | --- |
| DC Power Load | 51.8 |
| Boost Voltage | 53.5 |
| Float Voltage | 53.94 |

Alarm Limits

| Low Voltage | 46.3 |
| --- | --- |
| High Voltage | 59.5 |
| High Load | 80% |
| High Temperature | 30 °C |

Low Voltage, High Voltage, High Load and High Temperature alarms were triggered,

but only Low Voltage alarm was visible to SMC

------------------------------------------------------------------------------------------------------------

## Do Three Month Routine for Battery feeding NGA Equipment in Mountmellick

Temperature: 22 C

### Battery 1

Overall Voltage: 54.25

13.54

13.55

13.54

13.55

### Battery 2

Overall Voltage: 54.24 V

13.55

13.55

13.54

13.55

-------

## Do DC Power Routine for Rectifier feeding NGA Equipment in Mountmellick

| Rectifiers | 5 |
| --- | --- |
| DC Power Load | 23 |
| Boost Voltage | 54.5 |
| Float Voltage | 54.2 |

Alarm Limits

| Low Voltage | 47 |
| --- | --- |
| High Voltage | 58 |
| High Load | 80% |
| High Temperature | 28 °C |

--------------------------

Low Voltage, High Voltage, High Load and High Temperature alarms were triggered,

but only Low Voltage alarm was visible to SMC