Kilcormac (KRMA)

Tuesday 3 March 2026

10:32

+ Please clean/replace filter on KRMA-MSAN

+ Inspect FAN on FTTH node KRM1-F01A - Ensure air intake/exhaust clear

## Do Three Month Routine for Battery 1 in Kilcormac

The overall: 53.99

| Cell # | Voltage (V) | Cell # | Voltage (V) |
| --- | --- | --- | --- |
| 1 | 2.26 | 13 | 2.26 |
| 2 | 2.24 | 14 | 2.25 |
| 3 | 2.24 | 15 | 2.25 |
| 4 | 2.26 | 16 | 2.26 |
| 5 | 2.25 | 17 | 2.25 |
| 6 | 2.22 | 18 | 2.25 |
| 7 | 2.23 | 19 | 2.25 |
| 8 | 2.25 | 20 | 2.28 |
| 9 | 2.25 | 21 | 2.27 |
| 10 | 2.25 | 22 | 2.26 |
| 11 | 2.23 | 23 | 2.26 |
| 12 | 2.25 | 24 | 2.25 |

From <https://gemini.google.com/app/d6fda23163c68003>

## Do DC Power Routine in Kilcormac (Powec)

| Rectifiers | 5 |
| --- | --- |
| DC Power Load | 19.1 |
| Boost Voltage | 54 |
| Float Voltage | 54.0 |

Alarm Limits

| Low Voltage | 47 |
| --- | --- |
| High Voltage | 58 |
| High Load | 100% |
| High Temperature | 30 °C - not wired |

Low Voltage, High Voltage and High Load, alarms were tested, 2 alarm were visible.

## 2A Do Three Month Routine for Battery Feeding NGA Equipment in Kilcormac

Temperature: 17 C

Overall voltage: 54.57

| 13.64 | 13.61 | 13.62 | 13.59 |
| --- | --- | --- | --- |

## Do Three Month Routine for Battery Feeding NGA Equipment in Kilcormac (Power One)

| Rectifiers | 5 |
| --- | --- |
| DC Power Load | 14 |
| Boost Voltage | 54.1 |
| Float Voltage | 54.1 |

Alarm Limits

| Low Voltage | 47 |
| --- | --- |
| High Voltage | 58 |
| High Load | 80% |
| High Temperature | 30 °C |

Low Voltage, High Voltage, High Load, and High Temperature alarms were tested, but only one Low voltage